# TENDER SPECIFICATION

# RECIRCULATING WATER CHILLER, 20 kW

### 1. Scope of Supply

Procurement of Re-circulating Chiller, 20 kW cooling capacity for laser cooling application at RRCAT, Indore.

| Item No. | Category | Item Description | Key Specifications | Qty |
| --- | --- | --- | --- | --- |
| 1 | Main Equipment | Re-circulating Chiller, 20 kW | Cooling = 20 kW @10°C | 1 No |
| 2 | Accessories | Water hose pipe, 1/2” × 3m, insulated with nitrile rubber, with connectors | 1/2” BSP, nitrile rubber insulation full length | 2 Nos |
| 3 | Accessories | Quick connect coupling, 1/2” to 1/2” | 1/2” BSP | 2 Nos |

### 2. Bidder Qualification Criteria (BQC)

2.1 Main Equipment Manufacturer: The OEM must have supplied at least 2 units of similar-capacity (20 kW or higher) re-circulating chillers to government / PSU / reputed organizations in the last 3 years. Supporting documents (Purchase Orders / Completion Certificates) must be provided as verifiable evidence. The OEM must hold valid ISO 9001:2015 and ISO 14001:2015 certifications. Copies of valid certificates must be enclosed with the bid.

2.2 Accessories / Subcomponents Sourcing: Only OEM or Authorized dealers are allowed to bid. The authorized dealers must submit OEM authorization certificate for the main chiller equipment on OEM letterhead.

### 3. Technical Requirements

3.1 Main Equipment

| Parameter | Specification |
| --- | --- |
| Cooling Capacity | 20 kW @ 10°C outlet temperature |
| Flow Rate | ≥75 LPM (Stainless Steel 304 pump) |
| Pump Head Pressure | ≥4 bar |
| Temperature Set Range | Ambient to 2°C |
| Temperature Control Accuracy | ±1°C |
| Refrigerant | R404a / R-407C / R-22 or equivalent |
| Compressor | Sealed type, energy efficient |
| Tank Capacity | ≥60 L (SS 304) |
| Tank Insulation | 25–50 mm Nitrile Rubber or PUF sheets |
| Material of Construction — Pump & Tank | SS 304 (corrosion resistant) |
| Material of Construction — Outer Frame | MS |
| Operating Environment | Forced air cooling, ambient ≤40°C |
| Electrical Supply | 415V ±10%, three-phase, 50 Hz |
| Water Inlet / Outlet Coupling | 1” BSP |
| Mains Cable | Heavy duty, 3-core, 5 m length |
| Portability | Heavy duty castor wheels (user removable) with locking arrangement |
| Controls | Digital temperature indicator cum controller |
| Filter | Dust filter mesh |
| Finish / Coating | Standard off-shelf finish |

3.2 Accessories

| Item | Specification |
| --- | --- |
| Water Hose Pipe (×2) | 1” bore, 3 m length, nitrile rubber insulation on full length, with inlet/outlet connectors |
| Quick Connect Coupling (×2) | 1” BSP to 1” BSP |

3.3 Safety Features

| Feature | Requirement |
| --- | --- |
| Water Low Level Trip | Automatic shutdown on low water level |
| Over Temperature Trip | Automatic shutdown on over-temperature |
| Overload Alarm | Alarm on compressor / pump overload |
| Trip Alarm | Visual / audible trip indication |
| Water Freezing Prevention | Protection against water freezing in cooling circuit |

### 4. Quality Assurance, Testing & Documentation

4.1 Testing: - The item shall be tested at RRCAT, Indore upon receipt. All requirements mentioned in Section 3 will be tested. Final acceptance and payment release shall be contingent on successful testing at RRCAT.

4.2 Documentation to be submitted with the bid:

Document Requirement: —

Duly filled and signed compliance sheet (Section 6 of this specification), product catalogue with make & model specified, OEM authorization certificate and past installations evidence.

Note: Make and model number of all catalogued items shall be verifiable from the manufacturer’s official website.

### 5. Delivery Terms

| Term | Detail |
| --- | --- |
| Delivery Timeline | 12 weeks from PO date |
| Packaging | Standard commercial packaging suitable for road transit |
| Warranty | 12 months from date of final acceptance at RRCAT facility |

### 6. Vendor Mandatory Compliance Sheet

Instructions: Bidders must indicate compliance clearly for every parameter. ‘Yes/No/Complied’ NOT ALLOWED. Attach supporting documents for each claim. Bids with incomplete or unsigned sheets may be summarily rejected.

| No. | Parameter | Requirement | Supporting Document | Vendor Compliance |
| --- | --- | --- | --- | --- |
| 6.1 | Make & Model Verification | Make & model number verifiable from manufacturer’s website |  |  |
| 6.2 | Quality Certifications | Valid ISO 9001:2015 + ISO 14001:2015 |  |  |
| 6.3 | OEM Authorization | OEM authorization certificate on OEM letterhead |  |  |
| 6.4 | Cooling Capacity | 20 kW @10°C |  |  |
| 6.5 | Flow Rate | ≥75 LPM (SS 304 pump) |  |  |
| 6.6 | Minimum Temperature | 2°C |  |  |
| 6.6 | Pump Head Pressure | ≥4 bar |  |  |
| 6.7 | Tank Capacity | ≥60 L, SS 304 |  |  |
| 6.8 | Refrigerant | R404a / R-407C / R-22 or equivalent |  |  |
| 6.9 | Electrical Supply | 415V ±10%, 3-phase, 50 Hz |  |  |
| 6.10 | Pipe | Water hose pipes |  |  |
| 6.11 | Coupling | Quick connect coupling |  |  |

Signature of Bidder: ___________________

Company Seal: ________________________

Date: __________________________________